## ATU_Schedule_with_Areas_Served
UNIT ID | AREA SERVED by Yo | AREA SERVED | Network | Device Instance | Source RTU | MAX CFM | MIN CFM | HEATING CFM | BRANCH DUCT SIZE | BOX SIZE | EAT | ELECTRIC REHEAT LAT | kW | CONTROL | V/PH
ATU-1.1 | Lobby 101 | Lobby 101 | 100 | 1100003 | RTU-1 | 800 | 200 | 200 | 14 | 12 | 55 | 95 | 2.5 | SCR | 208/1
ATU-1.2 | Dining Room 102 | Dining 102 | 100 | 1100004 | RTU-1 | 1500 | 350 | 350 | 16 | 14 | 55 | 95 | 4.5 | SCR | 208/3
ATU-1.3 | Kitchen Area 103 | Dining 102 | 100 | 1100005 | RTU-1 | 1500 | 350 | 350 | 16 | 14 | 55 | 95 | 4.5 | SCR | 208/3
ATU-1.4 | Women's Restroom 104 | Kitchen | 100 | 1100006 | RTU-1 | 1500 | 150 | 150 | 16 | 14 | 55 | 95 | 2 | SCR | 208/1
ATU-1.5 | Men's Restroom 105 | Kitchen | 200 | 1200003 | RTU-1 | 1500 | 150 | 150 | 16 | 14 | 55 | 95 | 2 | SCR | 208/1
ATU-1.6 | Gaming Area 106 | Gaming 106 | 100 | 1100007 | RTU-1 | 1300 | 500 | 450 | 16 | 14 | 55 | 76 | 3 | SCR | 208/1
ATU-1.7 | Security Area 107 | Gaming 106 | 100 | 1100008 | RTU-1 | 1400 | 450 | 450 | 16 | 14 | 55 | 76 | 3 | SCR | 208/1
ATU-1.8 | Men's Restroom 108 | Gaming 106/Promo 115/Cashier | 100 | 1100009 | RTU-1 | 1500 | 500 | 450 | 16 | 14 | 55 | 76 | 3 | SCR | 208/1
ATU-1.9 | Women's Restroom 109 | Gaming 106 | 100 | 1100010 | RTU-1 | 1200 | 450 | 450 | 12 | 10 | 55 | 76 | 3 | SCR | 208/1
ATU-1.10 | Mantrap Area 111 | Gaming 106 | 100 | 1100011 | RTU-1 | 1200 | 450 | 450 | 12 | 10 | 55 | 76 | 3 | SCR | 208/1
ATU-1.11 | Gaming Cage 112 | Gaming 106 | 100 | 1100012 | RTU-1 | 1200 | 450 | 450 | 12 | 10 | 55 | 76 | 3 | SCR | 208/1
ATU-1.12 | Cashier Area 113 | Office 126 | 200 | 1200004 | RTU-1 | 300 | 100 | 100 | 10 | 8 | 55 | 95 | 1 | SCR | 120/1
ATU-1.13 | Promo Area 114 | Bait andTackle | 200 | 1200005 | RTU-1 | 1000 | 300 | 300 | 12 | 10 | 55 | 95 | 4 | SCR | 208/3
ATU-1.14 | Area near Gaming Cage | Security | 200 | 1200006 | RTU-1 | 300 | 100 | 100 | 10 | 8 | 55 | 95 | 1 | SCR | 120/1
ATU-2.1 | Area near Beverages/Retail 203 | Lobby 201 | 400 | 1400003 | RTU-2 | 800 | 200 | 200 | 12 | 10 | 55 | 95 | 2.5 | SCR | 208/1
ATU-2.2 | Gaming Area 202 | Gaming 202 | 400 | 1400004 | RTU-2 | 1200 | 800 | 800 | 12 | 10 | 55 | 71 | 4 | SCR | 208/3
ATU-2.3 | Lobby Area 201 | Gaming 202 | 400 | 1400005 | RTU-2 | 700 | 400 | 400 | 10 | 8 | 55 | 75 | 2.5 | SCR | 208/1
ATU-2.4 | Men's Restroom 205 | Gaming 202 | 400 | 1400006 | RTU-2 | 700 | 400 | 400 | 10 | 8 | 55 | 75 | 2.5 | SCR | 208/1
ATU-2.5 | Women's Restroom 207 | Gaming 202 | 300 | 1300003 | RTU-2 | 1400 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-2.6 | Employee Key/Storage 208 | Gaming 202 | 300 | 1300004 | RTU-2 | 1400 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-2.7 | Server Room 211 | Gaming 202 | 400 | 1400007 | RTU-2 | 1500 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-2.8 | Mantrap Area 212 | Gaming 202 | 400 | 1400008 | RTU-2 | 1100 | 800 | 800 | 12 | 10 | 55 | 71 | 4 | SCR | 208/3
ATU-2.9 | Gaming Cage 213 | Gaming 202 | 300 | 1300005 | RTU-2 | 1400 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-2.10 | Storage Area 214 | Count Room 216/Main Count Room 217/Cashier 215 | 400 | 1400009 | RTU-2 | 700 | 200 | 300 | 10 | 8 | 55 | 97 | 4 | SCR | 208/3
ATU-2.11 | Cashier Area 215 | Gaming 202 | 300 | 1300006 | RTU-2 | 1400 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-2.12 | Count Room 216 | Employee Key/STG 208 | 300 | 1300007 | RTU-2 | 300 | 100 | 100 | 8 | 6 | 55 | 87 | 1 | SCR | 120/1
ATU-2.13 | Main Count Room 217 | Gaming 202 | 300 | 1300008 | RTU-2 | 1200 | 800 | 800 | 12 | 10 | 55 | 71 | 4 | SCR | 208/3
ATU-2.14 | Service Corridor 218 | Beverages/Retail 203 | 400 | 1400010 | RTU-2 | 300 | 100 | 100 | 8 | 6 | 55 | 87 | 1 | SCR | 120/1
ATU-2.15 | Employee Restroom 219 | Gaming 202 | 400 | 1400011 | RTU-2 | 1400 | 800 | 800 | 16 | 14 | 55 | 71 | 4 | SCR | 208/3
ATU-3.1 | Clubhouse 301 | Clubhouse 301 | 400 | 1400012 | RTU-2 | 1200 | 200 | 450 | 12 | 10 | 55 | 71 | 4 | SCR | 208/3